{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":9,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MV1"]
[]
[]
[]
[]
["","","","","","AZAS71M2V1B","AZAS100M7V1B","AZAS125M7V1B","AZAS140M7V1B"]
["Dimensionet","Njësia","","Lartësia","mm","770","990","990","990"]
["","","","Gjerësia","mm","900","940","940","940"]
["","","","Thellësia","mm","320","320","320","320"]
["Pesha","Njësia","","","kg","60","70","70","78"]
["Kompresori","Lloji","","","","Kompresor rrotullues i mbyllur hermetikisht","Kompresor rrotullues i mbyllur hermetikisht","Kompresor rrotullues i mbyllur hermetikisht","Kompresor rrotullues i mbyllur hermetikisht"]
["Diapazoni i funksionimit","Ftohje","Ambienti","Min.","°CDB","-5","-5","-5","-5"]
["","","","Maks.","°CDB","46","46","46","46"]
["","Ngrohje","Ambienti","Min.","°CWB","-15","-15","-15","-15"]
["","","","Maks.","°CWB","15.5","15.5","15.5","15.5"]
["Niveli i fuqisë së zhurmës","Ftohje","","","dBA","65","70","71","73"]
["","Ngrohje","","","dBA","","","71 (1)","73 (1)"]
["Niveli i presionit të zhurmës","Ftohje","","Nom.","dBA","46","53","53","54"]
["","Ngrohje","","Nom.","dBA","47","57","57","57"]
["Agjenti ftohës","Lloji","","","","R-32","R-32","R-32","R-32"]
["","Mbushja","","","kg","2.45","2.60","2.60","2.90"]
["","GWP","","","","675","675","675","675"]
["","Mbushja","","","tCO2Eq","1.65","1.76","1.76","1.96"]
["Lidhjet e tubacioneve","Lëngu","","Dia. jasht.","mm","9.52","9.52","9.52","9.52"]
["","Gazi","","Dia. jasht.","mm","15.9","15.9","15.9","15.9"]
["","Gjatësia e tubacioneve","Maks.","OU - IU","m","30","30","30","30"]
["","","Sistemi","Ekuivalent","m","50","50","50","50"]
["","","","Pa ngarkesë","m","30","30","30","30"]
["","Mbushje shtesë me agjent ftohës","","","kg/m","Shihni manualin e instalimit","Shihni manualin e instalimit","Shihni manualin e instalimit","Shihni manualin e instalimit"]
["","Ndryshimi i nivelit","IU - OU","Maks.","m","30.0","30.0","30.0","30.0"]
["","","IU - IU","Maks.","m","0.5","0.5","0.5","0.5"]
["Aksesore Standarde","Installation manual","","","","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2"]
["Furnizimi me energji","Faza","","","","1~","1~","1~","1~"]
["","Frekuenca","","","Hz","50","50","50","50"]
["","Tensioni","","","V","220-240","220-240","220-240","220-240"]
["Rryma - 50 Hz","Amperët maksimalë të siguresës (MFA)","","","A","20","25","32","32"]
["Aksesore Standarde","Peel off F-gas label","","","","1"]
["Shënime","","","","","","","(1) - Sipas ENER Lot 21","(1) - Sipas ENER Lot 21"]