{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":32,"n_cols":7,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQ-C"]
[]
[]
[]
[]
["","","","","","RZQ250C7Y1B","RZQ200C7Y1B"]
["Dimensionet","Njësia","","Lartësia","mm","1,680","1,680"]
["","","","Gjerësia","mm","930","930"]
["","","","Thellësia","mm","765","765"]
["Pesha","Njësia","","","kg","184.0","183.0"]
["Kompresori","Lloji","","","","Kompresor spiral i mbyllur hermetikisht","Kompresor spiral i mbyllur hermetikisht"]
["Diapazoni i funksionimit","Ftohja","Ambienti","Min.","°CDB","-5.0","-5.0"]
["","","","Maks.","°CDB","46.0","46.0"]
["","Ngrohje","Ambienti","Min.","°CWB","-15.0","-15.0"]
["","","","Maks.","°CWB","15.0","15.0"]
["Sound power level","Ftohje","","","dBA","78.0","78.0"]
["","Ngrohje","","","dBA","78.0","78.0"]
["Agjenti ftohës","Lloji","","","","R-410A","R-410A"]
["","Ngarkesa","","","kg","9.3","8.3"]
["","GWP","","","","2,087.5","2,087.5"]
["Lidhjet e tubacioneve","Lëngu","","Dia. jasht.","mm","12.70","9.52"]
["","Gazi","","Dia. jasht.","mm","22.2","22.2"]
["","Gjatësia e tubacioneve","Maks.","OU - IU","m","100","100"]
["","","Sistemi","Pa ngarkesë","m","30","30"]
["Aksesore Standarde","Manual instalimi","","","","1","1"]
["","Tuba për lidhjen","","","","4","4"]
["Power supply","Faza","","","","3N~","3N~"]
["","Frekuenca","","","Hz","50","50"]
["","Tensioni","","","V","380-415","380-415"]
["Rryma - 50 Hz","Amperët maksimalë të siguresës (MFA)","","","A","25","25"]
["Shënime","","","","","(1) - Furnizimi me energji i njësisë së brendhme FDQ është më vete","(1) - Furnizimi me energji i njësisë së brendhme FDQ është më vete"]
["","","","","","(2) - Shiko skicat e veçantë për të dhënat e skicave elektrike","(2) - Shiko skicat e veçantë për të dhënat e skicave elektrike"]